COMTRAXX® CP305-C

MEDICS®

Alarm and test combination with fully graphic 5’ touch display for visual and audible indication of alarm messages with new value behavior. Standard and programmable texts for (medical) IT systems, EDS and RCMS applications. Parameterisation and input of message texts via web server or network.

12 digital inputs for displaying messages, status of external systems, e.g. medical gases or BSV/USV

2 relay contacts freely parameterizable and switchable via the display

Standards:

DIN VDE 0100-710 (VDE 0100 Teil 710)

IEC 60364-7-710

DIN EN 61557-8

DIN EN 60601-1-8

Device features:

Fully graphic 5’ display with plain text display

Touch operation

Glass front, 3.2 mm tempered glass, hygienically smooth and easy to clean and disinfect

RGB LED for signaling the system status

Display can be automatically dimmed and switched off to save energy

Start screen can be parameterized, up to 4 measured values, time or individual texts

IP66 protection of the glass operating surface

IP54 protection when installed in the wall (TÜV certification)

Buzzer for alarms, IT system messages, EDS, RCMS, general alarms and medical gas alarms

Adjustable buzzer tones and volume

Energy storage for bridging 2 s downtime without data loss

Communication via BMS bus or Modbus RTU with Bender devices

12 digital inputs, galvanically isolated, operating mode can be set for each channel, individual message texts can be programmed

Status of the digital inputs can be displayed on the BMS via Modbus TCP

Collective signaling or by channel

Relay contacts can be used as switches and pushbuttons, switchable via display

Visual and acoustic alarm in the event of a fault

Display as plain text

Standard messages for IT systems, changeover devices, ISOMETER®, EDS and RCMS systems,

500 individual alarms programmable per channel

10 images/ icons can be displayed individually per alarm

50 test addresses for triggering tests on Bender measuring devices

1,000 entries in the non-volatile history memory

Parameterisation via menu on the device or web server via Ethernet direct connection or network TCP/IP

Can be maintained remotely in a network, reduces time spent in patient areas

Silent alerting in combination with at least one other Bender display device

Timer/countdown timer for medical staff

Supply voltage: AC 24 V, 50..60 Hz; DC 24 V

Interfaces: RS485/BMS bus and Modbus RTU with Bender Smart Connect, RJ45

Inputs: 12 digital inputs, potential-free

Relay contacts: 2 relay contacts, changeover contact

Version: without flush-mounted housing

Pre-configuration at the factory:

Setting device addresses, alarm addresses and test addresses

Including factory programming of the alarm text

Based on project planning or detailed customer specifications

Accessories:

Flush-mounted box B923710

Cavity wall installation kit: B923711

Ethernet connector kit: B95100152

Surface-mounted housing: B95100153
MK800-Retrofit Kit: BF95100154

Reference to source of supply:

Bender GmbH & Co. KG

Londorfer Straße 65

D-35305 Grünberg

Telefon: 06401/807-0

vertrieb.inland@bender.de

www.bender.de

Type: CP305-C

Order number: B22030051