CP915

At the interface between humans and machines, alarm indicator and operator panels play a key role. Their task consists in emitting a visual and acoustic alarm and converting information from the system into comprehensible operating and handling instructions. This applies in particular to critical operating situations. The CP9xx Control Panel offers the user a solution that meets the requirements of modern medical locations as well as industrial und purpose-built buildings

Standards:
The execution corresponds:
DIN VDE 0100-710(VDE 0100 Teil 710):2012-10
IEC 60364-7-710:2002-11

Features:
 - 24“ Touchscreen with glass surface. 
 - Integration of Bender and third party devices
 - All devices can be displayed, served and monitored
 - Forced alarming via Bender Bus (BMS), maximum 5s between alert and information on the display
- Remote Access possible
 - Communication via Ehternet, BCOM, Bender Bus (BMS), Modbus TCP/RTU. Other interfaces possible
 - fanless
 - Representation and naming of all control elements and alarm, warning, operating and failure messages individually and as required
 - Parametrization of different acoustic alarm sounds
 - Individuell introduction per alert possible
 - Individuell visualization possible
 - Colours and pictures with individuell customer skins
 - Cleaning mode with display lock, alerting is forced farther
 - Alternating alert messages
 - Remote Testing of IP-Systems
 - Subsequent changes to the display and control elements and the texts of the visualization are possible during operation
 - Backup: Ex- and import possible for the whole project
 - integrated webserver and editor integrated
 - native integration of surgical lights on request

System-functions:
 - Access via webserver
 - Password protection with different access rights
 - System overview over all connected devices
 - Displaying of all alerts, measurements and parameters of conncected devices
 - individuell texts for all connected devices 
 - E-Mail-messaging in case of failure
 - History logger with 20.000 entries, export function (.csv-Format), time stamp, recording of alerts, tests switching states (ATICS) with min. and max. values, quit time of alerts
 - 30 data logger with 10.000 data points
 - read out of history and data logger via network
 - Parametrization of connected Bender devices 
 - Locigal function editor
 - Third party devices via Modbus
 - System documentation with all parameters
 - Backup (Ex- and Import) 
 - replacement and maintenance in one operation-break
 - 24/7 operation
 - Maintenance remote access


Visualization: 
 - Access via integrated webserver 
 - Configuration required, device is delivered without presetting
 - Visualization is customizable

Technical Data:
Display size: 15 Zoll, capazitive touchscreen
Resolution: hd-ready
OS: Linux
Supply voltage: 100...240 VAC
Power consumption: <35 W
Energy storage (CPU) >15 s
Buzzer: integrated
Interfaces:
 - 2 x RS-485 with galvanic separation
 - 2 terminating resistors, switchable
 - protocols: BMS, Modbus RTU (Master)
 - Ethernet (RJ45)
 - protocols: BCOM, Modbus TCP (Client/Server), SMTP, NTP, DHCP, http, ...
 - 2 x USB
[bookmark: _Hlk528667366] - 1 x I2C
[bookmark: _Hlk528667391] - 1 Audio in
 - 1 Audio out
 - 12 digital inputs / galvanic seperated
 - 1 Relais (N/O, N/C) 2 A
Front: Resistant to cleaning agents and disinfectants
Glass colour: grey 
Dimensions: 505 x 350 x 92 mm (BxHxD)
Mounting: Flush mounting 
Scope of delivery: incl. Flush mounting wall box
Degree of protection: IP 54

Manufacturer: 
Bender GmbH & Co. KG
Londorfer Str. 65   
35305 Grünberg

Typ: CP915
oder gleichwertiges Fabrikat, das alle zuvor beschriebenen Eigenschaften und Funktionen erfüllt.
Der Nachweis darüber ist zu erbringen.
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